## Slide 1: GRADOS DE PROTECCIÓN DE CARCAZAS Y CAJAS DE EQUIPOS Y APARATOS
La norma internacional CEI 529, de la Comisión Electrotécnica Internacional establece una codificación numérica a través de la cual se definen las características de los grados de protección que la envolvente, carcaza o caja, de un equipo proporciona tanto desde el punto de vista de protección a las personas frente a la posibilidad de alcanzar partes energizadas en el interior del equipo o aparato, como desde el punto de vista de penetración de elementos extraños al equipo como cuerpos, polvos o agua que interfieran con su funcionamiento y/o le provoquen daños.
La caracterización de los grados de protección se establece mediante un código formado por las letras IP (índice de protección) seguidas de una combinación de dos cifras, cuyo significado se establece en las tablas 1.I a 1.V siguientes. Debe tenerse en cuenta que la primera cifra tiene dos significados que se indican en las tablas 1.I y 1.II, estos significados son complementarios y de aplicación simultánea.

## Slide 2
Los equipos o aparatos calificados según esta norma llevarán marcado sobre su carcaza o caja el número de código correspondiente, siguiendo la disposición mostrada a continuación

## Slide 3: En el caso de la primera cifra característica 3,4,5 ó 6 la protección contra acceso a partes energizadas se satisface si se mantiene la distancia adecuada. Los requerimientos de esta Tabla se aplicarán simultáneamente con los de la Tabla 1.II.

## Slide 4: TABLA 1.II

## Slide 5
TABLA 1.III

## Slide 6
(1) El chorro de agua se obtendrá de una boquilla de  = 6,3 mm que entregará un caudal de 12,5 l/min  5%; el diámetro del chorro será 40 mm a 2,5 m del objeto.
(2) Idem 1 pero caudal será 100 l/min  5% y diámetro del chorro 120 mm a 2,5 m. En ambos casos, 1 y 2, el chorro se aplicará durante 3 minutos a una distancia 2,5 m  d  3 m.
(3) La muestra se sumergirá en agua con una altura de 150 mm sobre su cubierta si h = (alto de la muestra)  850 mm y (1000 – h) si h  850 mm. Tiempo de la prueba 1 minuto, temperatura muestra = temperatura del agua  5%.
Algunas normas consideran la aplicación de letras adicionales que refuerzan o aclaran la calidad del grado de protección de un equipo, o bien restringen su aplicación a cierto tipos de equipos o condiciones particulares de aplicación. Estos índices adicionales se detallan en las Tablas 1.iV y 1.V siguientes.

## Slide 7: Tabla 1.IV

## Slide 9: NEMA Enclosure Types [From NEMA 250-1997] In Non-Hazardous Locations, the specific enclosure Types, their applications, and the environmental conditions they are designed to protect against, when completely and properly installed, are as follows: Type 1 - Enclosures constructed for indoor use to provide a degree of protection to personnel against incidental contact with the enclosed equipment and to provide a degree of protection against falling dirt. Type 2 - Enclosures constructed for indoor use to provide a degree of protection to personnel against incidental contact with the enclosed equipment, to provide a degree of protection against falling dirt, and to provide a degree of protection against dripping and light splashing of liquids. Type 3 - Enclosures constructed for either indoor or outdoor use to provide a degree of protection to personnel against incidental contact with the enclosed equipment; to provide a degree of protection against falling dirt, rain, sleet, snow, and windblown dust; and that will be undamaged by the external formation of ice on the enclosure. Type 3R - Enclosures constructed for either indoor or outdoor use to provide a degree of protection to personnel against incidental contact with the enclosed equipment; to provide a degree of protection against falling dirt, rain, sleet, and snow; and that will be undamaged by the external formation of ice on the enclosure. Type 3S - Enclosures constructed for either indoor or outdoor use to provide a degree of protection to personnel against incidental contact with the enclosed equipment; to provide a degree of protection against falling dirt, rain, sleet, snow, and windblown dust; and in which the external mechanism(s) remain operable when ice laden. Type 4 - Enclosures constructed for either indoor or outdoor use to provide a degree of protection to personnel against incidental contact with the enclosed equipment; to provide a degree of protection against falling dirt, rain, sleet, snow, windblown dust, splashing water, and hose-directed water; and that will be undamaged by the external formation of ice on the enclosure.

## Slide 10: Type 4X - Enclosures constructed for either indoor or outdoor use to provide a degree of protection to personnel against incidental contact with the enclosed equipment; to provide a degree of protection against falling dirt, rain, sleet, snow, windblown dust, splashing water, hose-directed water, and corrosion; and that will be undamaged by the external formation of ice on the enclosure. Type 5 - Enclosures constructed for indoor use to provide a degree of protection to personnel against incidental contact with the enclosed equipment; to provide a degree of protection against falling dirt; against settling airborne dust, lint, fibres, and flyings; and to provide a degree of protection against dripping and light splashing of liquids. Type 6 - Enclosures constructed for either indoor or outdoor use to provide a degree of protection to personnel against incidental contact with the enclosed equipment; to provide a degree of protection against falling dirt; against hose-directed water and the entry of water during occasional temporary submersion at a limited depth; and that will be undamaged by the external formation of ice on the enclosure. Type 6P - Enclosures constructed for either indoor or outdoor use to provide a degree of protection to personnel against incidental contact with the enclosed equipment; to provide a degree of protection against falling dirt; against hose-directed water and the entry of water during prolonged submersion at a limited depth; and that will be undamaged by the external formation of ice on the enclosure. Type 12 - Enclosures constructed (without knockouts) for indoor use to provide a degree of protection to personnel against incidental contact with the enclosed equipment; to provide a degree of protection against falling dirt; against circulating dust, lint, fibres, and flyings; and against dripping and light splashing of liquids. Type 12K - Enclosures constructed (with knockouts) for indoor use to provide a degree of protection to personnel against incidental contact with the enclosed equipment; to provide a degree of protection against falling dirt; against circulating dust, lint, fibres, and flyings; and against dripping and light splashing of liquids. Type 13 - Enclosures constructed for indoor use to provide a degree of protection to personnel against incidental contact with the enclosed equipment; to provide a degree of protection against falling dirt; against circulating dust, lint, fibres, and flyings; and against the spraying, splashing, and seepage of water, oil, and non-corrosive coolants.